## Impact of Factors
COOLING PROJECT
Trend of various parameters based on changes in Advanced Geometry factors of Unilab coil selection program
Default value and impact on various parameters with value more than default value
Sr. No. | Parameters \ Factor | Fin corr. Factor The default value is 1. If the value increases / decreases, the coefficient of partial exchange air side increases / decreases. |  |  | Coeff. Factor Tube side The default value is 1. If the value increases / decreases, the coefficient of partial exchange inside the tube increases / decreases. |  |  | Corr. Factor Friction factor The default value is 1. If the value increases / decreases, the inner tube side pressure drop increases / decreases. |  |  | Friction factor Air side The default value is 1. If the value increases / decreases, the air side pressure loss increases / decreases. |  |  | Rid / Aum Factor Surface The default value is 1. If the value increases / decreases, the heat exchange surface in the calculation increases / decreases and so the power increases / decreases. |  |  | Red. Area Pass. Tube The default value is 1. If the value increases / decreases, the passage area of the pipe decreases / increases. |  |  | Latent Air Friction Factor The default value is 1. If the value increases / decreases, the load losses relating to condensed increases / decreases (you have to apply only to cooling coils of air) |  |  | Delta F Factors table RESERVED UNILAB | Slope Fin Corr. Factor RESERVED UNILAB | Slope Fact. Tube Side Coeff. RESERVED UNILAB | Slope Corr. Factor Friction Factor RESERVED UNILAB | Slope Fact. Air Friction RESERVED UNILAB | Tube Inner Surfaces Ratio The default value is 1. If the value increases / decreases, the tube internal exchange surface increases / decreases. |  |  | Security Factor The default value is 1. If the value increases / decreases, the capacity increases / decreases. |  |  | Factor For the Sensible Capacity The default value is 0,6. If the value increases / decreases, the sensitive capacity decreases / increases (you have to apply only to cooling coils of air).
|  | Partial Exchange Coefficient Air Side | Default value | New Value | Partial Exchange Coefficient Fluid Side | Default value | New Value | Water / refrigerant side water drop | Default value | New Value | Air side pressure drop | Default value | New Value | Capacity | Default value | New Value | Fluid Velocity | Default value | New Value | Pressure losse relating to condensed air | Default value | New Value | Unchecked | 1 | 1 | 1 | 1 | Partial Exchange Coefficient Fluid Side | Default value | New Value | Capacity | Default value | New Value | Capacity Sensitive | Default value | New Value
|  |  | 1 | 1.15 |  | 1 | 1.15 |  | 1 | 1.15 |  | 1 | 1.25 |  | 1 | 1.15 |  | 1 | 1.15 |  | 1 | 1.15 | Unchecked | 1 | 1 | 1 | 1 |  | 1 | 1.5 |  | 1 | 1.15 |  | 0.6 | 0.7
| DIRECT VALUE CHANGED |  | Increase |  |  | Increase |  |  | Increase |  |  | Increase |  |  | Increase |  |  | Decrease |  |  | Increase | [7 empty] | Increase |  |  | Increase |  |  | Decrease
1 | Sensible heat removal capacity |  |  | Increase |  |  | Increase |  |  | No change |  |  | No change |  |  | Increase |  |  | Decrease |  |  | No change |  | No change | No change | No change | No change |  |  | Increase |  |  | Increase |  |  | Decrease
2 | Latent heat removal capacity |  |  | Increase |  |  | Increase |  |  | Increase |  |  | Increase |  |  | Increase |  |  | Decrease |  |  | Increase |  | No change | No change | No change | No change |  |  | Increase |  |  | Increase |  |  | Increase | Increase
3 | Air side pressure drop |  |  | Increase |  |  | No change |  |  | No change |  |  | Increase |  |  | Increase |  |  | Decrease |  |  | Increase |  | No change | No change | No change | No change |  |  | No change |  |  | Increase |  |  | Increase | No change
4 | Water / refrigerant side water drop |  |  | Increase |  |  | Increase |  |  | Increase |  |  | No change |  |  | Increase |  |  | Decrease |  |  | No change |  | No change | No change | No change | No change |  |  | Increase |  |  | Increase |  |  | Increase
5 | Leaving air temperature
5.1 | Dry Bulb |  |  | Decrease |  |  | Decrease |  |  | No change |  |  | No change |  |  | Decrease |  |  | Increase |  |  | No change |  | No change | No change | No change | No change |  |  | Decrease |  |  | Decrease |  |  | Increase
5.2 | Wet Bulb |  |  | Decrease |  |  | Decrease |  |  | No change |  |  | No change |  |  | Decrease |  |  | Increase |  |  | No change |  | No change | No change | No change | No change |  |  | Decrease |  |  | Decrease |  |  | No change
5.3 | Coil ADP |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  | No change | No change | No change | No change |  |  | No change |  |  | No change |  |  | No change
0
6 | Leaving water / refrigerant temperature |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  |  | No change |  | No change | No change | No change | No change |  |  | No change |  |  | No change |  |  | No change
Note - Select the impact of each factor on various parameters - by default it is selected as No change
We have no idea for most of the factors as what it represents and when it is to be applied meaning corrected as more than or less than the default value